IEC 61850 AND IEC 62439 TECHNICAL INTEROPERABILITY TEST – BILBAO 2014

| Author: | SoC-e |
| --- | --- |
| Revised: | SoC-e |
| Version: | 140701 |

Bilbao, July 1st 2014

# REVISION HISTORY

| Ver . | Date | Responsible | Comments |
| --- | --- | --- | --- |
| 140609 | 2014/06/09 | AA | Initial version |
| 140613 | 2014/06/13 | AA | Logistics and Hotel Info |
| 140617 | 2014/06/17 | MI, AG | Test-Plan initial proposal |
| 140625 | 2014/06/25 | MI, AG | Revised according to new topology proposal without RSTP |
| 140701 | 2014/07/01 | MI | Added Flexibilis and Ingeteam to the pre-testing topologies |

Table 1 : Changes in the document

# INDEX

REVISION HISTORY	ii

INDEX	iii

FIGURE INDEX	4

TABLE INDEX	5

1	INTRODUCTION	6

1.1	Scope	6

1.2	UCAIug Booth Topology 2014	7

1.3	Participants Role and Equipments	9

1.4	Test Premises Layout	9

2	TEST PLAN	10

2.1	CIGRE2014 IEC62439/IEC61850 Pre-Testing	10

2.1.1	Test 1A : Equipment physical interconnection	12

2.1.2	Test 1B: Network testing	12

2.1.3	Test 1D: Running IEC61850 demo application (Breaker Failure)	12

2.2	Optional Test 1: IEEE1588 with IEC62439 over CIGRE2014 Network Topology	13

2.2.1	Optional Test 1A. Basic Test	14

2.2.2	Optional Test 1B. Open and close HSR ring	14

2.2.3	Optional Test 1C. Network impairments.	15

2.3	Optional Test 2: 1GE HSR IEEE1588 P2P	17

2.3.1	Optional Test 2A. Basic Test	18

2.3.2	Optional Test 2B. Open and close RSTP and HSR rings	18

2.3.3	Optional Test 2C. Network impairments.	19

3	LOGISTICS AND OTHER ADDITIONAL INFORMATION	21

3.1	INTEROPERABILITY PREMISES LOCATION	22

3.2	SHIPMENTS LOGISTICS	22

3.2.1	Shipment address	22

3.2.2	Dates for packages collect/delivery	22

3.3	HOTEL INFORMATION	23

# FIGURE INDEX

Figure 1: Conceptual Topology	7

Figure 2: Network Topology	8

Figure 3: Pre-Testing. Topology I	10

Figure 4: Pre-Testing. Topology II	11

Figure 5: Pre-Testing. Topology III	13

Figure 6: Pre-Testing. Topology IV	17

Figure 7: NH Bilbao Hotel Location	24

Figure 8: Hesperia Hotel Location	25

Figure 9: Ercilla Hotel Location	26

# TABLE INDEX

Table 1 : Changes in the document	ii

# INTRODUCTION

## Scope

TBD

## UCAIug Booth Topology 2014

Figure 1: Conceptual Topology

Figure 2: Network Topology

## Participants Role and Equipments

TBD

## Test Premises Layout

TBD

# TEST PLAN

## CIGRE2014 IEC62439/IEC61850 Pre-Testing

Figure 3: Pre-Testing. Topology I

Figure 4: Pre-Testing. Topology II

### Test 1A : Equipment physical interconnection

Test set-up

Network topology is shown in Figure 3.

Redundancy in HSR ring is according to IEC 62439-3 Chap 5.

Test sequence

- Check link status and autonegotiation results in every device.

Expected results

All devices are physically connected to their neighbours.

### Test 1B: Network testing

Test set-up

Network topology is shown in Figure 3.

Redundancy in HSR ring is according to IEC 62439-3 Chap 5.

A data stream is injected in the net (audio/video) and replayed in another point.

Test sequence

- Start video broadcasting and check it is playing in client.

- Break HSR ring.

- Check video/audio playback.

- Close HSR ring.

- Check video/audio playback.

Video Stream Configuration

TBD

Note: We could use instead of Video Streaming, File Trasnfer as well.

Expected results

Data stream is received in the player without stopping in steps 2 and 4.

### Test 1D: Running IEC61850 demo application (Breaker Failure)

TBD

## Optional Test 1: IEEE1588 with IEC62439 over CIGRE2014 Network Topology

Figure 5: Pre-Testing. Topology III

### Optional Test 1A. Basic Test

Test set-up

Network topology is shown in Figure 5. GrandMaster is connected to a single network and this through a Transparent Clock to the HSR ring.

Redundancy in HSR ring is according to IEC 62439-3 Chap 5. PTP configuration used is Utility Profile IEC 62439-3/CDV:2014 Annex B

- Layer 2 Ethernet

- Multicast

- P2P delay calculation mechanism

- 2-step

- PTP management and signaling disabled

- 1 announce/s, 1 sync/s, 1 pdelay_req/s

Test sequence

- Switch all slaves on.

- Check that all slaves are synchronized to the GM using a PPS signal.

Expected results

All slaves should be synchronized below 1us.

### Optional Test 1B. Open and close HSR ring

Test set-up

Network topology is shown in Figure 5. GrandMaster is connected to RSTP network and this through a StateLess Transparent Clock to the HSR ring.

Redundancy in HSR ring is according to IEC 62439-3 Chap 5. PTP configuration used is Utility Profile IEC 62439-3/CDV:2014 Annex B

- Layer 2 Ethernet

- Multicast

- P2P delay calculation mechanism

- 2-step

- PTP management and signaling disabled

- 1 announce/s, 1 sync/s, 1 pdelay_req/s

Test sequence

- Switch all slaves on.

- Check that all slaves are synchronized to the GM using a PPS signal.

- Break HSR ring.

- Check synchronization.

- Close HSR ring.

- Check synchronization.

Expected results

All slaves should be synchronized below 1us in steps 2, 4 and 6.

### Optional Test 1C. Network impairments.

Test set-up

Network topology is shown in Figure 5. GrandMaster is connected to RSTP network and this through a Transparent Clock to the HSR ring. Traffic generator is connected to the RSTP ring.

RSTP redundancy is per IEEE 802,1D-2004 Chap. 17. Redundancy in HSR ring is according to IEC 62439-3 Chap 5. PTP configuration used is Utility Profile IEC 62439-3/CDV:2014 Annex B

- Layer 2 Ethernet

- Multicast

- P2P delay calculation mechanism

- 2-step

- PTP management and signaling disabled

- 1 announce/s, 1 sync/s, 1 pdelay_req/s

Traffic load description

- Multicast

- Packet length RFC 2544

Test sequence

- Switch all slaves on.

- Check that all slaves are synchronized to the GM using a PPS signal.

- Inject traffic by steps (10%, 20%, 40%, 60%, 80%, 90%).

- Check synchronization in each step.

Expected results

All slaves should be synchronized below 1us during all test duration.

Extra impairment tests

Using a net impairment equipment inserted in either in RSTP ring or in HSR ring, several impairments could be forced such as packet dropping, bit error, duplicated packets or packet delay variation. This tests can be determined in situ under the requirements of the attendees.

## Optional Test 2: 1GE HSR IEEE1588 P2P

Figure 6: Pre-Testing. Topology IV

### Optional Test 2A. Basic Test

Test set-up

Network topology is shown in Figure 6. GrandMaster is connected through a StateLess Transparent Clock to the HSR ring.

Redundancy in HSR ring is according to IEC 62439-3 Chap 5. PTP configuration used is Utility Profile IEC 62439-3/CDV:2014 Annex B

- Layer 2 Ethernet

- Multicast

- P2P delay calculation mechanism

- 2-step

- PTP management and signaling disabled

- 1 announce/s, 1 sync/s, 1 pdelay_req/s

Test sequence

- Switch all slaves on.

- Check that all slaves are synchronized to the GM using a PPS signal.

Expected results

All slaves should be synchronized below 1us.

### Optional Test 2B. Open and close RSTP and HSR rings

Test set-up

Network topology is shown in Figure 6. GrandMaster is connected through a Transparent Clock to the HSR ring.

Redundancy in HSR ring is according to IEC 62439-3 Chap 5. PTP configuration used is Utility Profile IEC 62439-3/CDV:2014 Annex B

- Layer 2 Ethernet

- Multicast

- P2P delay calculation mechanism

- 2-step

- PTP management and signaling disabled

- 1 announce/s, 1 sync/s, 1 pdelay_req/s

Test sequence

- Switch all slaves on.

- Check that all slaves are synchronized to the GM using a PPS signal.

- Break HSR ring.

- Check synchronization.

- Close HSR ring.

- Check synchronization.

Expected results

All slaves should be synchronized below 1us in steps 2, 4, and 6.

### Optional Test 2C. Network impairments.

Test set-up

Network topology is shown in Figure 6. GrandMaster is connected through a StateLess Transparent Clock to the HSR ring.

Redundancy in HSR ring is according to IEC 62439-3 Chap 5. PTP configuration used is Utility Profile IEC 62439-3/CDV:2014 Annex B

- Layer 2 Ethernet

- Multicast

- P2P delay calculation mechanism

- 2-step

- PTP management and signaling disabled

- 1 announce/s, 1 sync/s, 1 pdelay_req/s

Traffic description

- Multicast

- Packet length RFC 2544

Test sequence

- Switch all slaves on.

- Check that all slaves are synchronized to the GM using a PPS signal.

- Inject traffic by steps (10%, 20%, 40%, 60%, 80%, 90%).

- Check synchronization in each step.

Expected results

All slaves should be synchronized below 1us during all test duration.

Extra impairment tests

Using a net impairment equipment inserted in HSR ring, several impairments could be forced such as packet dropping, bit error, duplicated packets or packet delay variation. This tests can be determined in situ under the requirements of the attendees.

# LOGISTICS AND OTHER ADDITIONAL INFORMATION

## INTEROPERABILITY PREMISES LOCATION

## SHIPMENTS LOGISTICS

### Shipment address

All the packages for the Interop in Bilbao, must be delivered to the following address:

Att: D. LUIS URIA (Laboratorio de Tecnología Electrónica)

ESCUELA TECNICA SUPERIOR DE INGENIERIA (FACULTY OF ENGINEERING UPV/EHU)

PLAZA ING. TORRES QUEVEDO, 1

48013 BILBAO

SPAIN

Telephone: +34 644064541

### Dates for packages collect/delivery

All the packages sent to this event will be stored in a specific premise in the Faculty of Engineering of Bilbao. The interop event will be help in the same Faculty.

The dates opened to collect packages are:

From July 7th to July 15th

The transport companies can collect the packages at the same address in the following dates:

From July 16th to July 23rd

(Except Saturdays and Sundays)

If anyone requires any special arrangement regarding the logistics, please contact aitzol.zuloaga@ehu.es

## HOTEL INFORMATION

NH COLLECTION VILLA DE BILBAO HOTEL

This is the suggested first option.

Address: Gran Vía, 87 | 48011 Bilbao | SPAIN

Phone: +34 94 441 60 00, ge.dearrese@nh-hotels.com, www.nh-hotels.com

Hotel class: 4 stars

Prices per room and night (reservation till 2014/7/2):

In:             14/07/2014

Out:            16/07/2014

Single room:  82 euros

Double room:       93 euros

Buffet breakfast:        included

Value-addeed tax (VAT) Not included:        10%

To book phone or mail (nhvilladebilbao@nh-hotels.com) and give the reference "IEC 61850 AND IEC 62439 TECHNICAL INTEROPERABILITY TEST".

Figure 7: NH Bilbao Hotel Location

HESPERIA ZUBIALDE HOTEL

Address: Camino de la Ventosa, 34, 48013 BILBAO, SPAIN

Phone: +34 94 400 81 00, hotel@hesperia-zubialde.com, www.nh-hotels.com

Hotel class: 4 stars

Figure 8: Hesperia Hotel Location

ERCILLA HOTEL

Address: Calle de Ercilla, 37-39, 48011 Bilbao, Vizcaya

Phone: +34 944 70 57 00, http://www.hotusa.com/hotels/spain/vizcaya-bilbao/bilbao/hotel-ercilla.html

Hotel class: 4 stars

Figure 9: Ercilla Hotel Location